ANNEXURE – C

Reply to Point. No. 3

- Methodology for carrying out Load flow studies:

- Base case PSSE (Power System Simulator for Engineering) file of FY 2022-23 with existing network is considered and FY 2028-29 PSSE case file is prepared duly considering the proposed generation, transmission network and estimated load.

- The load flow studies are carried out for FY 2028-29 of 5th Control Period duly considering the generation of 16004.2 MW, transmission network and estimated load of 21962 MW for FY 2028-29 using PSSE software.

- The line loadings, transformer loadings, bus voltages and short circuit values are observed and confirmed as per prescribed limits of Transmission Planning criteria. Further, (N-1) contingency for all the transformers and lines at 400kV & 220kV level is also ensured.

- Assumptions and parameters for carrying out Load flow studies:

- Generation Availability for various generators are considered as follows:

Thermal 	–	85 %

Hydel 	– 	70 %

Solar 		– 	85 %

Wind 		– 	55 %

- Conductor Parameters and Thermal loading limits are considered as per CEA Manual on Transmission Planning Criteria, 2023.

- The standards adopted for load flow studies are already mentioned at para 2.3 (A) to (G) in Chapter-2 of Resource Plan Report at page no.31