ORDER NO: 165, DT:09.12.2013.

TRANSMISSION CORPORATION OF ANDHRA PRADESH LIMITED

From,								To

The Superintending Engineer,				Smt M.Suseela,

TL&SS Circle, APTRANSCO,			            D.No.20/658, Balaji Street,

KADAPA.							Madras Road,

Kadapa – 516 002.

Lr.No. SE/TL&SS.KFP/ADE-T/AET1/F.Doc/D.No.2658 /13, Dt.05– 12-2013.

Sir,

Sub:- APTRANSCO – TL&SS Circle, Kadapa - Painting of M.S. Towers in 132 KV Yerraguntla-

Proddatur DC line from Loc No. 17 to 52 with one coat of red oxide paint and one coat

of Aluminium paint of Asian or Nerolac Make- Letter of Intent – Issued – Reg.

Ref:-Memo.No.CE/KDPZone/KDP/Tech/ADET2/AET3/F.28/D.No.1770/13,Dt.23.07.13.

****

The rates offered by you  towards carrying out “Painting of M.S. Towers in 132 KV Yerraguntla -Proddatur DC line from Loc No. 17 to 52 with one coat of red oxide paint and one coat of Aluminium paint of Asian or Nerolac Make ” are hereby accepted.  Pending conclusion of the agreement, you are requested to contact the Divisional Engineer TL&SS/ Yerraguntla  and take up  the work duly following  the  conditions as mentioned below.

- The entire towers should be thoroughly scratched using wire brushes uniformly without any scales of rust and painting of towers to be taken up after approval of the concerned.

- The paints should be of prime grade – I paints and shall be procured from reputed company of Asian or Nerolac make only and got approved by the concerned ADE/AE before commencement of the work.

- The preparation of paint should be done at work site only during the application of paint at the time of painting only.

- The entire tower should be uniformly painted with Red oxide paint using brushes and care should be taken while painting at joints, angles and corners etc.

- After completion of Red oxide paint, approval shall be taken from the Superintending Engineer/TL&SS/Kadapa for further proceeding of Aluminium painting.

- After taking necessary approval, aluminum paint should be uniformly done duly maintaining   standard painting thickness using paint brushes only, duly leaving 1 feet of legs at the bottom of towers without Aluminium paint.

- After completion of the Aluminum paint, black paint should be applied to the bottom of the tower up to a height of 1 feet.

- All the precautionary measures should be taken during the execution of work.

- The painting should withstand for all seasonal changes and weather conditions.

- To ensure quality of workmanship and quality in materials through effective supervision while carrying out painting works of MS structures of 220 KV and 132KV towers  i.e. during mixing of paint and execution of work.  Departmental person should be available at the work spot till the completion of painting work. Contractor should ensure uniform overall painting thickness about 87microns and arrange for checking the same during the inspection of painting work by APTRANSCO officials.

- Ensure that a gap of minimum three (3) days should be maintained between application of red oxide paint and aluminum paint.

- Painting works should be carried out during dry weather conditions only.

- The contractor should submit weekly program of working locations in advance to the Divisional  Engineer/TL&SS/Yerraguntla for arranging quality control inspections.  All the works shall be executed as per the program fixed by the Divisional Engineer/TL&SS/Yerraguntla.

- The contractor shall take risk insurance policies for all the labour employed by him in the work.  Failure to do so, that entire responsibility on the payment of compensation risks with the contractor itself, in case of any accidents.

- The work will be carried out in accordance with APDSS and Indian standard code of practice.

- The whole work is to be completed within 3 months from the date of handing over of site to the contractor by the department.

Further you are requested to pay security deposit for an amount of Rs.13,420.00(Rupees Thirteen thousand four hundred and twenty only) and through demand draft drawn in favour of the Superintending Engineer / TL&SS/ APTRANSCO/Kadapa and approach this office within 15 days  with a non judicial stamped paper of worth Rs.100-00 for entering into agreement.

Encl: Copy of the schedule.

Accepted all the terms and conditions of the LOI.

SUPERINTENDING ENGINEER

TL & SS CIRCLE : KADAPA.

CONTRACTOR

Copy to the Divisional Engineer/TL & SS / Yerraguntla

Copy to the Asst.Divisional Engineer/Lines/Yerraguntla.	*

Copy to the Asst. Engineer/ Lines/Yerraguntla.

* They are requested to execute the above work as per the conditions of the letter of intent without fail and submit the work order number for entering into the agreement.

Copy submitted to the Chief Engineer/Kadapa Zone/Kadapa.

Copy to the Accounts Officer/TL&SS/Kadapa.

SCHEDULE

Name of the work : Painting of M.S. Towers in 132 KV Yerraguntla -Prodatur DC line from Loc No. 17 to 52 with one coat of red oxide paint and one coat of Aluminium paint of Asian or Nerolac Make.

| Sl. No. | Description | Qty | Rate per in Rs. | Amount in Rs |
| --- | --- | --- | --- | --- |
| 1 | Painting of towers with single coat of red oxide paint of 1st grade including scratching and cleaning of towers. |  |  |  |
|  | One coat of 1st grade red oxide paint including labour charges for scratching and cleaning of towers including cost of paint, brushes etc., | 115.569MT | 1549.64 | 179090.34 |
| 2 | Painting of towers with one coat of aluminium paint using aluminium paint 1st grade containing 3.6 Kg of aluminium paste for 18 Ltrs. of thinner including cost of paint, cost of brushes, labour charges etc., complete |  |  |  |
|  | First coat of 1st grade aluminium paint duly scratching and cleaning of towers including labour charges, cost of paint, brushes etc., | 115.569MT | 2474.56 | 285982.42 |
|  | Sub-Total |  |  | 465072.76 |
|  | WCT @ 3.5% on Sub-Total |  |  | 16277.54 |
|  | Service Tax @ 12.36% on 60% on Sub-Total (*) |  |  | 34489.79 |
|  | Grand Total |  |  | 515840.09 |
|  | Or say |  |  | 515840.00 |

(Rupees Five lakh Fifteen  thousand eight hundred and forty only)

(*) 50% of service tax amount should be paid by the APTRANSCO  and the remaining 50% amount paid by the contractor.

SUPERINTENDING ENGINEER

TL&SS CIRCLE: KADAPA.